|  | ......................... pcs. .............................. € .............................. € GEZE electric spindle drive E 250 NT for a smoke and heat extraction system For daily aeration and ventilation and safe and fast smoke and heat exhaust and smoke extraction on vertically or angled installed, inward and outward opening bottom-hung, top-hung and side-hung casements as well as for light domes and skylights. Electric spindle drive E 250 NT in 24 V version. The drive must be activated via a micro-processor. A distinction can be made between alarm and ventilation operating speed. Stroke arresting device and ventilation speed can be programmed as required via software. Load switch-off and end-position cut-off must be implemented electronically. The control is carried out via the GEZE emergency power control unit in the event that the smoke and heat extraction system is triggered. Daily use of the ventilation function is carried out using the GEZE vent switch. Sealing via electronically defined pressure. Synchronised multiple operation of up to 3 drives must be guaranteed without additional external module. Activation and adjustment of the Syncro function is by means of integrated dip switches without additional programming being necessary Technical data: Stroke in mm: 100/150/200/230/300/500/750/1000* Tensile force and pressure: 750 N/750 N Voltage: 24 V DC / 230 V AC with external mains adapter Current consumption: RWA (18 V) 1.0 A, ventilation (24 V) 0,9 A With stroke 500: RWA (18 V) 1.3 A, ventilation (24 V) 1,1 A Enclosure rating: IP 65 Ambient temperature: -5 °C to +70 °C Connection cable: 2 m, silicon sheathed* * Special lengths on request GEZE electric spindle drive E 250 NT up to stroke length 500 mm is suitable for installation in GEZE SHEVs tested and certified in accordance with EN 12101-2. Version: ( ) Solo (permissible casement weight max. 100 kg) ( ) Syncro (permissible casement weight max. 200 kg) Type of window: ( ) Bottom-hung casement ( ) Top-hung casement ( ) Side-hung casement ( ) Skylight ( ) inward opening ( ) outward opening Casement dimensions: ......... mm width ......... mm height Casement material: ( ) Wood ( ) Aluminium ( ) Plastic Opening width: ........ mm or max. ....... mm (to be completed by the bidder) Colour: ( ) EV1 ( ) white RAL 9016 ( ) according to RAL ........ |
| --- | --- |
|  | ......................... pcs. .............................. € .............................. € ( ) Standard bracket for the primary closing edge ( ) Inward bracket for the primary closing edge ( ) Swivelling bracket for the secondary closing edge |
|  | ......................... pcs. .............................. € .............................. € Note: In order to guarantee the performance classes as set out in DIN EN 14351-1 with regard to wind load, sealing in the event of rain and air tightness, an additional locking mechanism must be planned on the window according to the specifications of the profile system manufacturer, e.g. GEZE Power lock. |
|  | ......................... pcs. .............................. € .............................. € Note: You also require an emergency power control unit GEZE E 260 N, THZ, THZ Comfort or MBZ 300 and accessories. |
|  | ......................... pcs. .............................. € .............................. € Installation and functional test Installation and functional test by an expert authorised by the manufacturer. |
|  | ......................... pcs. .............................. € .............................. € Start-up and official approval Official approval of the complete smoke and heat extraction system by an officially recognised expert, who also hands over the acceptance certificates. |
|  | ......................... pcs. .............................. € .............................. € Service maintenance - compact package Maintenance and testing of hold-open systems (optional position) Service package for maintenance and testing according to ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - Fault diagnosis and repair jobs during the contract period will be carried out at reduced hourly rates - Service technicians will be deployed within 24 hours of the message being received from Monday – Friday between 7 am and 5 pm without surcharges - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 2 years |
|  | ......................... pcs. .............................. € .............................. € Service maintenance - comfort package Service maintenance (optional position) Comfort service package for maintenance and accident prevention inspection in accordance with ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - Extension of the warranty to 36 months (condition: the maintenance contract is concluded 3 months after the commissioning date at the latest) - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - No separate charging for services and travel costs during the warranty period - No separate charging for consumables up to € 25 per maintenance - No separate charging for working hours when spare parts are replaced during the maintenance - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 3 years |
|  | ......................... pcs. .............................. € .............................. € Delivery and installation Wiring to be carried out on site by an electrical contractor according to the GEZE cable plan. Delivery, installation and commissioning through plant fitters or service partner. Safety analysis, instruction of the operator as to how the system works and handing over of the documentation. Annual maintenance and technical inspection by an expert authorised by the manufacturer incl. documentation of the inspection in an inspection log. |