|  | ......................... pcs. .............................. € .............................. € GEZE swing door automatic Slimdrive EMD-F, 1-leaf, for on-site fire or smoke control doors, (heed the DIBt guideline for hold-open systems) as a low-noise electromechanical swing door drive for internal and external doors, 70 mm overall height, with hold-open mechanism in accordance with DIN 18 263 Part 4, prepared for connection to release device, with adjustable spring force EN size 4-6, tested and certified in accordance with DIN 18650/EN 16005. Also suitable for opening doors manually without great effort (DIN 18040 optimised). Release in the event of an alarm through the self-sufficient GEZE release unit, with reset button for re-establishing standby after the alarm has been triggered, with release button ( ) flush-mounted ( ) surface-mounted, with mounting plate kit Intelligent digital control (Category 2 in accordance with DIN EN 954-1 and Performance Level “d” in accordance with DIN EN ISO 13849-1). Version: ( ) for use on fire or smoke control doors ( ) for use on single-action door without fire or smoke control requirement ( ) pushing, transom installation on the opposite hinge side with guide rail (EN 4-5) ( ) pushing, transom installation on the opposite hinge side with link arm (EN 4-6) ( ) pulling, transom installation on the hinge side with guide rail (EN 4-5) ( ) pulling, door leaf installation on the hinge side with guide rail (EN 4-5) Functions: Modes of operation: permanently open, automatic, shop closing, night “Shop closing” only in connection with an external programme switch Low-energy mode in accordance with DIN 18650/EN 16005, servo support to make the manual opening of swing doors easier, obstruction detection and reversing, diagnosis function and faulty memory, all settings are possible through the display programme switch Technical features: Dimensions: 70 x 120 mm (HxD), Mains connection: 230 V AC, 50/60 Hz, Door leaf width: max. 1400 mm, Door weight: max. 230 kg Door opening angle: approx. 110°, Opening and closing speed adjustable, Electrical latching action adjustable, Hold-open time adjustable from 0 to 60 seconds, Contour-controlled opening and closing Connection possibilities: Separate inputs for inner and outer sensors, emergency-stop switch, programme switch, motor lock, on-site door opener, power supply for external devices: 24 V DC, 1000 mA Wiring to be carried out on site by an electrical contractor according to the GEZE cable plan, commissioning to be carried out by plant fitters or service partner. In accordance with DIN 18650/EN 16005: - safety analysis must be carried out as a basis for planning and execution - maintenance and accident prevention inspection must be carried out at least once a year - the secondary closing edge of an automatic swing-leaf door must be secured If there is no protection, the safety analysis must refer to the residual risk. Protection of the secondary closing edge is to be carried out on site and is not part of the scope of supply of GEZE GmbH. We therefore recommend the use of a finger protection screen or round profiles to secure the secondary closing edge. Note on locking: Electric door opener, for releasing the door, 24 V DC, as counterpart to the latch lock, as well as lock switch contact for switching off the drive with the door locked (1 per drive) must be provided. Light alloy cover hood in the colour: ( ) anodised EV 1 ( ) RAL ..... |
| --- | --- |
|  | ......................... pcs. .............................. € .............................. € FT500-B Compact electric strike for fire protection doors in working current version, approved for use on fire protection doors, for universal use DIN left / right with radius latch adjustable 3mm, engagement depth: 6.5mm with twin coil technology, With bipolar EMC protective diode, Retention force: 8000 N Nominal voltage moment contact: 12-48 V AC/DC Nominal voltage permanent mode: 12 or 24 V AC/DC Current consumption: 100mA at 24 V VDS Class B Dimensions: 15.8 x 59.5 x 25.5 mm (W x H x D) Without strike plate |
|  | ......................... pcs. .............................. € .............................. € FT501-E Compact electric strike for fire protection doors in working current version, with signal processor and energy-saving mode, approved for use on fire protection doors, for universal use DIN left / right with radius latch adjustable 3mm, engagement depth: 6.5mm With bipolar EMC protective diode, Retention force: 8000 N Nominal voltage permanent mode: 8 - 24 V AC/DC Current consumption: 200mA (at 8 – 11 V) Current consumption: 50mA (at 12 – 24 V) VDS Class B Dimensions: 15.8 x 59.5 x 25.5 mm (W x H x D) Without strike plate |
|  | ......................... pcs. .............................. € .............................. € Optional position ( ) GEZE lock switch contact for switching the drive off with the door locked |
|  | ......................... pcs. .............................. € .............................. € Protection (optional position) GEZE GC 342 laser scanner, tested in accordance with EN 16005 / DIN 18650, mounted on the door leaf, to protect the swivelling range of interior and exterior doors in the opening and closing direction. Robust enough to handle all floor conditions (e.g. entrance mat, metal rail, dark and absorbing flooring, shiny and wet tiles, grating). With integrated wall blanking and dynamic main closing edge protection. Door leaf width: ....... mm ( ) GC 342 laser scanner kit (contains two sensors to protect both sides of the leaf) IP rating IP54, with optimised secondary closing edge protection. If fingers are very likely to be trapped, an additional mechanical solution on the secondary closing edge can be considered. The secondary closing edge protection near the door hinges must be carried out on-site or by the door manufacturer on the basis of the safety analysis. ( ) GC 342 for hinge side and GC 342+ for the opposite hinge side Combination of GC 342, IP rating IP54 for the hinge side and GC 342+, IP rating IP44 for the opposite hinge side. Each as an individual module (left and right variants) Version: ( ) stainless steel colour ( ) black ( ) white ( ) Fire protection kit - master-slave replacement cable which enables cables to be guided through 5 mm instead of 10 mm bore-holes. The drilling permit must be requested from the door manufacturer. Only available for GC 342: Protective cover to protect the laser scanner against interferences ( ) stainless steel colour ( ) black ( ) according to RAL ( ) Retrofit interface - retrofit circuit board for connection to door cables fitted on site |
|  | ......................... pcs. .............................. € .............................. € Protection (optional position) GEZE safety sensors kit, in sleek narrow strip with IP rating 52, type-approved in accordance with DIN 18650 / EN 16005, installed on the door leaf, for protecting the door's swivelling range in the opening and closing direction. With integrated wall blanking (kit contains 2 safety sensors for protecting both leaf sides) Door leaf width: ....... mm With asymmetrical double-leaf doors with EMD-IS, EMD F-IS: Door leaf width, active leaf: ....... mm Door leaf width, passive leaf: ....... mm ( ) GC 338 safety sensor kit for internal and external doors and all floor conditions (e.g. floor mat, metal rail, dark and absorbing flooring, shiny and wet tiles, grating). Version: ( ) EV1 ( ) according to RAL ( ) GC 338 rain cover to protect the safety sensor against interference caused by rain The secondary closing edge protection near the door hinges must be carried out on site or by the door manufacturer on the basis of the safety analysis. GEZE linkage element with integrated sensor, for the space-saving installation of sensor and link arm or guide rail on one plane, tested in accordance with DIN 18650/EN 16005, installed on the door leaf Version: ( ) GC GR, with integrated, two-part guide rail profile ( ) Adapter for the integration of the sensor strip with the link arm |
|  | ......................... pcs. .............................. € .............................. € Protection (optional position) GEZE emergency stop switch with glass pane and light, for switching off the mains voltage, enclosure rating IP 20 ( ) Surface-mounted ( ) Flush-mounted An emergency command device (emergency stop switch) is not essential in accordance with DIN 18650/EN 16005. |
|  | ......................... pcs. .............................. € .............................. € Activation (optional position) GC 308 radar movement detector with direction detection and cross-traffic fade-out for activation, IP 54 rating, multi-colour LED feedback Dimensions (WxHxD): 120 x 50 x 50 mm Version: ( ) black ( ) white ( ) stainless steel colour ( ) acc. to RAL ( ) outside ( ) inside Accessories: ( ) Ceiling installation kit ( ) Ceiling bracket ( ) exterior: weather hood |
|  | ......................... pcs. .............................. € .............................. € Activation (optional position) GC 302 radar movement detector with direction detection and cross-traffic fade-out for activation, IP rating IP 54 Dimensions (WxHxD): 176 x 62 x 52 mm Version: ( ) black ( ) acc. to RAL ( ) outside ( ) inside Accessories: ( ) Ceiling installation kit ( ) exterior: weather hood |
|  | ......................... pcs. .............................. € .............................. € Activation (optional position) GEZE elbow switch, plastic, IP rating IP 30 Dimensions: 90 x 180 x 23 mm ( ) white ( ) stainless steel ( ) optional transmitting module ( ) Surface-mounted ( ) Rear panel for attaching the elbow switch to glass (in connection with the transmitting module) or GEZE elbow switch, LS990, IP rating IP 30 Dimensions: 81 x 223 x 51 mm ( ) white ( ) stainless steel ( ) optional transmitting module ( ) Surface-mounted ( ) Flush-mounted or GEZE elbow switch, stainless steel, IP rating IP 65 Dimensions: 72 x 250 x 17 mm ( ) Surface-mounted or GEZE non-contact proximity switch (radar) Plastic with antimicrobial surface, IP rating IP65, multi-colour LED feedback, adjustable acoustic feedback. Additional input to actively change the LED colour. Dimensions: 80 x 80 mm ( ) Flush mounting 12 mm deep ( ) Surface mounting 21 mm deep ( ) Variant for WC or GEZE LED sensor push button, plastic, IP rating IP 69K round, diameter: 100 mm ( ) Flush-mounted ( ) Surface-mounted: mounting ring flat 4 mm ( ) Surface-mounted: mounting ring high 20 mm or GEZE LED sensor push button, glass, IP rating IP 69K round, diameter: 100 mm ( ) Flush-mounted ( ) Surface-mounted: mounting ring flat 4 mm ( ) Surface-mounted: mounting ring high 20 mm or GEZE LED sensor foot switch, glass, IP rating IP69K Dimensions: 100 x 100 x 3 mm ( ) flush-mounting ( ) vertically adjustable installation base for depths of up to 215 mm from the unfinished floor |
|  | ......................... pcs. .............................. € .............................. € Activation (optional position) GEZE wireless programme with secure rolling code encryption for wireless drive activation (range of approx. 30m in the building). Transmitters: ( ) Wireless transmitter with 1 key, enclosure rating IP 54 and wall fixing ( ) Wireless transmitter with 2 keys, enclosure rating IP 54 and wall fixing ( ) Wireless transmitter with 4 keys, enclosure rating IP 54 and wall fixing ( ) Wireless transmitter module for optional integration in the GEZE elbow switch Radio receiver: ( ) Radio receiver module with 2 outputs, 24 V, pulse mode or pulse and permanent mode for mounting in the drive or in a flush-mounted socket with enclosure rating IP 20 |
|  | ......................... pcs. .............................. € .............................. € Activation (optional position) GEZE GCER 300, 1-door SET Access control solution with RFID reader and PIN keypad in stand-alone operation for controlling one door (can be extended to 2 doors). RFID frequency 13.56 MHz. Authorisation is granted through master ID cards in combination with PIN keyboard directly at the reader. Up to 200 persons/ID cards can be authorised. If individual ID cards are lost or become faulty, they can simply be deleted from the system (selective deletion). Two authorisation types for short-time release or continuous release (office function). Configurable door release time. Variable PIN length. Communication between reader and control unit takes place by encrypted data transfer. Functions such as interlocking door system or dementia adjustable. Release buttons can be connected. Set comprising: 1 pc. GEZE GCER 300 I/O Box (ID no. 185707) 1 pc. GEZE GCVR 300 T, RFID reader flush-mounted (ID no. 185708) 2 pc. GEZE GCER 300 system card master (ID no. 185713) 10 pc. GEZE RFID ID card (ID no. 185711) Optional GEZE GCVR Touch 300 T, RFID reader flush-mounted (ID no. 187108) GEZE RFID key fob (ID no. 185712) GEZE GCER AP surface-mounted frame (Id. no. 130024) or GEZE GCER 300 Light, 1-door SET Access control solution with RFID reader and PIN keyboard in stand-alone operation with a relay output for controlling one door located in the secured inner area. RFID frequency 13.56 MHz. Authorisation is granted through master ID cards in combination with PIN keyboard directly at the reader. Up to 200 persons/ID cards can be authorised for short-time release. If individual ID cards are lost or become faulty, they can simply be deleted from the system (selective deletion). Configurable door release time. Variable PIN length. Communication takes place via encrypted data transfer. Set comprising: 1 pc. GEZE GCER 300 Light, RFID reader flush-mounted (ID no. 185710) 1 pc. GEZE GCER 300 system card master (ID no. 185713) 10 pc. GEZE RFID ID card (ID no. 185711) Optional GEZE RFID key fob (ID no. 185712) GEZE GCER AP surface-mounted frame (ID no. 130024) Accessories for GCER 300 / GCER 300 Light Plug-in power supply NT 1.0 A – 24 V DC (optional) Primary: 230 V AC, 50 Hz Secondary: 24 V DC (+/- 5 %) / 1 A (ID no. 130025) Power supply NT 1.1 A – 24 V DC flush-mounted (optional) For installation in deep standard flush-mounted boxes Primary: 230 V AC, 50 Hz Secondary: 24 V DC / 1.1 A (ID no. 151426) Power supply NT 1.5 A – 24 V DC HA (optional) For installation on top hat rails Primary: 230 V AC, 50 Hz Secondary: 21.6 – 26.4 V DC / 1.5 A (ID no. 151425) |
|  | ......................... pcs. .............................. € .............................. € GEZE RSZ 7 smoke switch control unit, suitable for installation on fire and smoke protection closers, extendable, with telescopic function, for bridging unfavourable lintel situations, 30 mm overall height, in GEZE design, with adaption of the alarm threshold, contamination indicator and integrated test button, integrated line monitoring to ceiling-mounted detector and manual trigger switch, for connection of GEZE hold-open devices, approved by DIBt as hold-open system for fire protection closers, EN 14637 compliant Connection: 230V AC Output voltage: 24 V DC, 250 mA For lintel height > 1 m, 2 additional ceiling-mounted detectors are needed. Colour: ( ) silver-coloured ( ) white ( ) stainless steel effect ( ) RAL ….. |
|  | ......................... pcs. .............................. € .............................. € GEZE smoke detector GC 152, 24 V, complete with base, tested in accordance with EN54-7, integrated line monitoring, conform to DIN EN 14637, can be connected to smoke switch control unit (2 pcs.) Colour: ( ) white |
|  | ......................... pcs. .............................. € .............................. € GEZE thermal detector GC 153, 24 V complete with base, tested in accordance with EN54-5, integrated line monitoring, conform to DIN EN 14637, can be connected to smoke switch control unit (2 pcs.) Colour: ( ) white |
|  | ......................... pcs. .............................. € .............................. € Operation (optional position) GEZE display programme switch in the AS 500 range for setting the mode of operation as well as for putting the drive into operation and setting parameters, with function keys, 2x 7-segment display, alphanumerical fault display, IP rating IP 40 Operating modes: permanently open, automatic, shop closing, night-locking ( ) Surface-mounted ( ) Flush-mounted or GEZE key programme switch for setting the operating mode, with function keys, LED matrix display, coded fault display, enclosure rating IP 40, suitable for switch programmes with 55 x 55 mm switch insert Modes of operation: off, permanently open, automatic, shop closing, night-locking ( ) Surface-mounted ( ) Flush-mounted or GEZE mechanical programme switch for setting the operating mode, with rotary knob, LED fault display, enclosure rating IP 40, suitable for switch programmes with 55 x 55 mm switch insert Modes of operation: off, permanently open, automatic, shop closing, night-locking ( ) Surface-mounted ( ) Flush-mounted or GEZE mechanical programme switch for setting the operating mode, with key, LED fault display, enclosure rating IP 40, suitable for switch programmes with 55 x 55 mm switch insert Modes of operation: off, permanently open, automatic, shop closing, night-locking ( ) Surface-mounted ( ) Flush-mounted |
|  | ......................... pcs. .............................. € .............................. € Operation (optional position) GEZE key switch to “lock” the programme switch to prevent unauthorised changing of the operating mode, enclosure rating IP 40 ( ) Surface-mounted ( ) Flush-mounted |
|  | ......................... pcs. .............................. € .............................. € Acceptance test (optional position) Acceptance test for the hold-open system and permanent attachment of the sign of approval |
|  | ......................... pcs. .............................. € .............................. € Service maintenance - compact package Maintenance and testing (option) Service package for maintenance and inspection in accordance with EN 16005, DIN 18650 Part 2 and ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - Fault diagnosis and repair jobs during the contract period will be carried out at reduced hourly rates - Service technicians will be deployed within 24 hours of the message being received from Monday – Friday between 7 am and 5 pm without surcharges - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 2 years e.g. GEZE compact service package |
|  | ......................... pcs. .............................. € .............................. € Service maintenance - comfort package Service maintenance (optional position) Comfort service package for maintenance in accordance with EN 16005, DIN 18650 Part 2 and ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - Extension of the warranty to 36 months (condition: the maintenance contract is concluded 3 months after the commissioning date at the latest) - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - No separate charging for services and travel costs during the warranty period - No separate charging for consumables up to EUR 25 per maintenance - No separate charging for working hours when spare parts are replaced during the maintenance - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 3 years |
|  | ......................... pcs. .............................. € .............................. € Service maintenance - exclusive package Service maintenance (optional position) Exclusive service package for servicing, maintenance in accordance with DIN 18650 Part 2 and ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - Extension of the warranty to 60 months (condition: the maintenance contract is concluded 3 months after the commissioning date at the latest) - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - Complete repair: no separate charging for repairs (parts and working hours) and travel costs during the contract run time - Online access for the client to the project and system data at the contractor’s - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 5 years |